## NC PLOT
| Project : |  |  |  |  | Tag:
| Octave Band: | 2 | 3 | 4 | 5 | 6 | 7
| Center Freq,Hz: | 125 | 250 | 500 | 1K | 2K | 4K
Input Sound Data Lw |  | 40 | 40 | 40 | 40 | 40 | 40 | 42 NC | 47 dBa | 7
Input Atten: |  | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 7
Atten Sound Data Lp |  | 35 | 35 | 35 | 35 | 35 | 35 | 37 NC | 42 dBa

## NC COMPARE
|  |  | Project : |  |  |  |  | Tag:
|  |  | Octave Band: | 2 | 3 | 4 | 5 | 6 | 7
Equipment Description |  |  | Center Freq,Hz: | 125 | 250 | 500 | 1K | 2K | 4K
| Input Sound Data Lw #1 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 52 NC | 57 dBa | 7
| Input Sound Data Lw #2 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 42 NC | 47 dBa | 7
|  | Input Atten: |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7
| Atten Sound Data Lp #1 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 52 NC | 57 dBa | 7
| Atten Sound Data Lp #2 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 42 NC | 47 dBa | 7

## RC PLOT
| Project : |  |  |  |  | Tag:
| Octave Band: | 2 | 3 | 4 | 5 | 6 | 7
| Center Freq,Hz: | 125 | 250 | 500 | 1K | 2K | 4K
Input Sound Data Lw |  | 40 | 40 | 40 | 40 | 40 | 40 | RC40 Hiss | 47 dBa
Input Attenuation |  | 5 | 5 | 5 | 5 | 5 | 5
Atten Sound Data Lp |  | 35 | 35 | 35 | 35 | 35 | 35 | RC35 Hiss | 42 dBa

## NC Calcs (hidden)
| NC PLOT | [8 empty] | RC PLOT
[8 empty] | Dominant |  | 125 | 250 | 500 | 1k | 2k | 4k
| 2 | 3 | 4 | 5 | 6 | 7 | NC | Band |  | 2 | 3 | 4 | 5 | 6 | 7 | RC
INPUT DATA NC | 20 | 28 | 35 | 39 | 41 | 42 | 42 | 7 | INPUT DATA Sound | 40 | 40 | 40 | 40 | 40 | 40 | 40
ATTEN DATA NC | 13 | 22 | 30 | 34 | 36 | 37 | 37 | 7 | RC Contour | 55 | 50 | 45 | 40 | 35 | 30
INPUT DATA DBA | 3.9 | 19.4 | 31.8 | 39 | 42.2 | 43 | 47 | dBa | Input - RC contour | -15 | -10 | -5 | 0 | 5 | 10
ATTN DATA DBA | -3.1 | 13.4 | 26.8 | 34 | 37.2 | 38 | 42 | dBA | Freq Group | MF |  |  | HF |  |  | QAI | Hiss
[9 empty] | Spectral Deviation |  | -8.2599 |  |  | 6.7401 |  | 15 | Objectionable
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 |  |  |  |  | 0 |  |  | 6.7401
[9 empty] | ATTEN DATA Sound | 35 | 35 | 35 | 35 | 35 | 35 | 35
[9 empty] | RC CONTOUR | 50 | 45 | 40 | 35 | 30 | 25
[9 empty] | Input - RC contour | -15 | -10 | -5 | 0 | 5 | 10
CURVE DATA | [8 empty] | Freq Group | MF |  |  | HF |  |  | QAI | Hiss
[9 empty] | Spectral Deviation |  | -8.2599 |  |  | 6.7401 |  | 15 | Objectionable
[9 empty] | QAI |  | 0 |  |  | 6.7401
NC15
15 | 125 | 2 | 36 | 2 | 30
| 250 | 3 | 29 | 3 | 25
| 500 | 4 | 22 | 4 | 20
| 1000 | 5 | 17 | 5 | 15
| 2000 | 6 | 14 | 6 | 10 |  |  |  | INPUT DATA DBA | 23.9 | 31.4 | 36.8 | 40 | 41.2 | 41 | 46 | dBa
| 4000 | 7 | 12 | 7 | 5 |  |  |  | ATTN DATA DBA | 18.9 | 26.4 | 31.8 | 35 | 36.2 | 36 | 41 | dBA
[10 empty] | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1
NC20
20 | 125 | 2 | 40 |  | 35
| 250 | 3 | 33 |  | 30 | [5 empty] | RC NUMBER
| 500 | 4 | 26 |  | 25 | [5 empty] | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 40 | 35
| 1000 | 5 | 22 |  | 20 |  |  |  |  | 125 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 55 | 50
| 2000 | 6 | 19 |  | 15 |  |  |  |  | 250 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 50 | 45
| 4000 | 7 | 17 |  | 10 |  |  |  |  | 500 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 45 | 40
[10 empty] | 1000 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 40 | 35
[10 empty] | 2000 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 35 | 30
[10 empty] | 4000 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 30 | 25
NC25
25 | 125 | 2 | 44 |  | 40
| 250 | 3 | 37 |  | 35
| 500 | 4 | 31 |  | 30
| 1000 | 5 | 27 |  | 25
| 2000 | 6 | 24 |  | 20 |  |  |  |  | RC NUMBER 15 30 25 20 15 10 5: Calcs for the NC compate data
| 4000 | 7 | 22 |  | 15
NC PLOT
Dominant
[12 empty] | 2 | 3 | 4 | 5 | 6 | 7 | NC | Band
[11 empty] | INPUT DATA #1 NC | 32 | 40 | 46 | 49 | 51 | 52 | 52 | 7
NC30 | [10 empty] | INPUT DATA #2 NC | 20 | 28 | 35 | 39 | 41 | 42 | 42 | 7
30 | 125 | 2 | 48 |  | 45 | [5 empty] | ATTEN DATA #1 NC | 32 | 40 | 46 | 49 | 51 | 52 | 52 | 7
| 250 | 3 | 41 |  | 40 | [5 empty] | ATTEN DATA #2 NC | 20 | 28 | 35 | 39 | 41 | 42 | 42 | 7
| 500 | 4 | 35 |  | 35 | [5 empty] | INPUT DATA #1 DBA | 15.9 | 31.4 | 42.8 | 49 | 52.2 | 53 | 57 | dBa
| 1000 | 5 | 31 |  | 30 | [5 empty] | INPUT DATA #2 DBA | 3.9 | 19.4 | 31.8 | 39 | 42.2 | 43 | 47 | dBa
| 2000 | 6 | 29 |  | 25 | [5 empty] | ATTN DATA #1 DBA | 15.9 | 31.4 | 42.8 | 49 | 52.2 | 53 | 57 | dBa
| 4000 | 7 | 28 |  | 20 | [5 empty] | ATTN DATA #2 DBA | 3.9 | 19.4 | 31.8 | 39 | 42.2 | 43 | 47 | dBa
[12 empty] | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1
NC35
35 | 125 | 2 | 52 |  | 50
| 250 | 3 | 45 |  | 45
| 500 | 4 | 40 |  | 40
| 1000 | 5 | 36 |  | 35
| 2000 | 6 | 34 |  | 30
| 4000 | 7 | 33 |  | 25
NC40
40 | 125 | 2 | 56 |  | 55
| 250 | 3 | 50 |  | 50
| 500 | 4 | 45 |  | 45
| 1000 | 5 | 41 |  | 40
| 2000 | 6 | 39 |  | 35
| 4000 | 7 | 38 |  | 30
NC45
45 | 125 | 2 | 60 |  | 60
| 250 | 3 | 54 |  | 55
| 500 | 4 | 49 |  | 50
| 1000 | 5 | 46 |  | 45
| 2000 | 6 | 44 |  | 40
| 4000 | 7 | 43 |  | 35
NC50
50 | 125 | 2 | 64 |  | 65
| 250 | 3 | 58 |  | 60
| 500 | 4 | 54 |  | 55
| 1000 | 5 | 51 |  | 50
| 2000 | 6 | 49 |  | 45
| 4000 | 7 | 48 |  | 40
NC55
55 | 125 | 2 | 67 |  | 70
| 250 | 3 | 62 |  | 65
| 500 | 4 | 58 |  | 60
| 1000 | 5 | 56 |  | 55
| 2000 | 6 | 54 |  | 50
| 4000 | 7 | 53 |  | 45
NC60
60 | 125 | 2 | 71 |  | 75
| 250 | 3 | 67 |  | 70
| 500 | 4 | 63 |  | 65
| 1000 | 5 | 61 |  | 60
| 2000 | 6 | 59 |  | 55
| 4000 | 7 | 58 |  | 50
NC65
65 | 125 | 2 | 75 |  | 80
| 250 | 3 | 71 |  | 75
| 500 | 4 | 68 |  | 70
| 1000 | 5 | 66 |  | 65
| 2000 | 6 | 64 |  | 60
| 4000 | 7 | 63 |  | 55

## User Guide
USER GUIDE
Anemostat's "NC & RC Sound Plotter v1.00" provides a simple user interface for display of sound data in a graphical format, and calculates Noise Criteria (NC) and Room Criteria (RC) values.
1. Compatable with Excel 2000 and later.
2. Top line of input data (Input Sound) may be sound power (Lw) or pressure (Lp) levels.
3. Input Attenuation data entry subtracts from the first line in each octave band.
4. Input values are decibels, dB.
5. Graphs are NOT automatically saved. You must manually save the data to a file name of your choice.
6. NC Plot includes the data for Input Sound, and the (Input minus Attenuation) data.
7. RC Plot and data is based on the RC Mark II method, and excludes low frequency center bands 16, 31.5, and 63 Hz. Analysis does NOT include low frequency rumble characteristics.
8. NC Compare allows graphical comparison of two sound sources, and includes both power level and pressure level plotting.
Disclaimer
This freeware is provided by Anemostat for personal use. Although every effort has been made to insure the accuracy and compatability of this program, Anemostat makes no claims as to its accuracy, and assumes no liability for its use.

## Revision Log (hidden)
Version | Description | Release Date
1 | Initial Release of Software | 2006-08-10