Contractor shall furnish and install Anemostat Model DJ Diffus-A-Jet air outlets of the jet discharge and/or diffusing type at each point indicated on the plans. The core of the outlet shall be rotatable so as to deliver air in a jet pattern or in a diffused pattern. The throw of the diffused pattern shall be approximately half that of the jet pattern at similar terminal velocities. Jet type diffusers without spread capability are not acceptable.

In either position, the axis of air flow may be varied up to 30° from the straight-forward in a full 360° arc. The outlet shall be attached to a mounting panel with mounting screws permitting 360° rotation. Up to four outlets may be attached to one mounting panel permitting multi-directional, as well as mixed jet and diffused patterns, from one location. (Optional) The outlet shall be directly mounted at the end of the round spiral duct where shown. 

The outlet and mounting panel shall be constructed from steel or aluminum as indicated.

The baked-on finish shall be Arctic white paint, or custom color, as scheduled.