Model AFDL
Door grilles shall be Anemostat Model AFDL non-vision, inverted Y type, of the sizes as scheduled, for 1-3/4” (1-3/8”, 2”, 2-1/8”) thick doors.  Grilles shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown.  Beveled borders shall be minimum 18 gauge material, with 22 gauge grille blades.  Inverted Y grille blades shall be spaced and formed for a sight proof design.  The frame mitered corners shall be arc welded along the joint from the back side.  Resistance welded frame construction is not approved. Assembly shall consist of an auxiliary frame with countersunk holes and screws that fastens to the grille core without drilling or screwing into door.  Position the side of grille without visible fastening screws towards corridor for security and aesthetic purposes.  Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect.  (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model CHDL-2F
Door grilles shall be Anemostat Model CHDL-2F non-vision, inverted V type, of the sizes as scheduled, for 1-3/4” (1-3/8”) thick doors.  Grilles shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown.  Beveled borders shall be minimum 18 gauge material, with 22 gauge grille blades.  Inverted V grille blades shall be spaced and formed for a sight proof design.  The frame mitered corners shall be arc welded along the joint from the back side.  Resistance welded frame construction is not approved.  Assembly shall consist of an auxiliary and core frame that attach directly to the door with screws thru countersunk holes.  Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect.  (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model FLDL-UL
Door grilles shall be Anemostat Model FLDL-UL non-vision type, and fire rated per test standards UBC 7.2-97 and UL10C by Underwriter’s Laboratories for 20, 45, 60, or 90 minutes.  Sizes to be as scheduled, for 1-3/4” (up to 2-1/8”) thick doors. Application of grilles for the specification installation and listing/rating requirements shall be the responsibility of the installing contractor. Grille shall have gang operated, pivoting blades that are held open with a replaceable fusible link, and shall close when link melts. Internal operating springs shall be stainless steel.  Grilles shall be constructed from steel or 304/316 stainless steel as shown. Border and grille blades shall be minimum 18 gauge material. The frame mitered corners shall be arc welded along the joint from the back side. Resistance welded frame construction is not approved. Assembly shall consist of an auxiliary frame with countersunk holes and screws that fastens to the grille core without drilling or screwing into door. Position the side of grille without visible fastening screws towards corridor for security and aesthetic purposes.  Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect.  (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces).

Model ADL
Door grilles shall be Anemostat Model ADL non-vision, adjustable type. Sizes to be as scheduled, for 1-3/4” (1-3/8”) thick doors.  Grilles shall have manually adjustable, pivoting, gang operated blades for full open or full closed positions. Internal operating springs assist in keeping blades fully closed and shall be stainless steel. Grilles shall be constructed from steel or 304/316 stainless steel as shown.  Border and grille blades shall be minimum 18 gauge material. The frame mitered corners shall be arc welded along the joint from the back side. Resistance welded frame construction is not approved. Assembly shall consist of an auxiliary frame with countersunk holes and screws that fastens to the grille core without drilling or screwing into door. Position the side of grille without visible fastening screws towards corridor for security and aesthetic purposes. Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect.  (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces).

Model AFDL-T
No sight grille core shall be Anemostat Model AFDL-T non-vision, inverted Y type, of the sizes as scheduled, and installed by the contractor as shown. Grille cores shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown.  22 gauge core blades shall be spaced and formed for a sight proof design. Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect. (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model CHDL
No sight grille core shall be Anemostat Model CHDL non-vision, inverted V type, of the sizes as scheduled, and installed by the contractor as shown. Grille cores shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown.  22 gauge core blades shall be spaced and formed for a sight proof design. Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect.  (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model DRDL
Dark Room Door grilles shall be Anemostat Model DRDL non-vision, inverted V type, of the sizes as scheduled, for 1-3/4” (1-3/8”) thick doors, or “half-pair” for ducted installations. Grilles shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown. Beveled borders shall be minimum 18 gauge material, with 20 gauge grille blades.  Inverted V grille blades shall be spaced and formed for a sight proof design. The frame mitered corners shall be arc welded along the joint from the back side. Resistance welded frame construction is not approved.  Grilles attach to mounting surface with screws thru countersunk holes. Finish shall be flat black or other color as selected by the architect. (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model CHDL-1F
No sight grilles shall be Anemostat Model CHDL-1F non-vision, inverted V type, of the sizes and installation configuration as scheduled. Grilles shall be constructed from steel, 304 or 316 stainless steel, or aluminum as shown.  Beveled borders shall be minimum 18 gauge material, with 22 gauge grille blades, and shall attach directly to the mounting surface with screws thru countersunk holes. Inverted V grille blades shall be spaced and formed for a sight proof design.  The frame mitered corners shall be arc welded along the joint from the back side.  Resistance welded frame construction is not approved. Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect. (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).

Model FDLS
Grilles shall be Anemostat Model FDLS non-vision, split Y type, of the sizes as scheduled, for 1-1/8”+ thick doors, or “half-pair” for ducted installations.  Grilles shall be constructed from minimum 18 gauge steel, 304 or 316 stainless steel, or aluminum as shown. The frame mitered corners shall be arc welded along the joint from the back side. Resistance welded frame construction is not approved. Grilles attach to mounting surface with screws thru countersunk holes. Finish shall be baked-on Anemostat Arctic White, or other color as selected by the architect. (Optional – Stainless steel units shall have a satin polish finish on all exposed surfaces)(Optional – Aluminum units shall be mill finish or anodized as scheduled).