SV2 – MAXIMUM SECURITY GRILLE 
3/16” X 3/16” OPENINGS

Contractor shall furnish and install security grille S-Vent® type SV2 as herein specified or where shown on plans. The unit shall be provided by Anemostat and will be of all steel assembled and welded construction. The grille shall be made of 14-gauge steel with the outer perimeter (face flange) stamped to raise the grille 5/16” from the wall or ceiling. The edge of the face flange shall be manufactured with a beveled slope. The edge shall rest flat (± .003”) on the wall or ceiling. The throat of the grille shall be 
1-7/16” in depth comprised of horizontal “S” channel blades and vertical mullions to create rigid 3/16” x 3/16” openings. The grille will be secured to a rear mounting duct collar using threaded rods attached to coupling nuts on the back of grille. The SV2 will be finished with a beige powder coat preceded by a multistage wash and surface preparation process.