## ATU Signals
Air Terminals
Velocity Wing Signal Generator 1.00
Control Type |  | Input Data |  |  | Airflow Data
|  | Inlet Size: | 8 |  | Signal Max: | 0.47892 | ∆P, in wg.
|  | Sensor Type: | Velocity Wing |  | Signal Min: | 0.083146 | ∆P, in wg.
|  | Max CFM: | 600 |  | K-Factor: | 867
|  | Min CFM: | 250 |  | Inlet Area: | 0.34907 | ft2
|  | Altitude, ft: | 0 |  | Max CFM Velocity: | 1718.8734 | FPM
[5 empty] | Min CFM Velocity: | 716.1972 | FPM
|  | Input Data |  |  | Airflow Data
|  | Inlet Size: | 14 |  | Airflow Rate: | 987.6 | CFM
|  | Sensor Type: | Velocity Wing |  | Air Velocity: | 923.8418 | FPM
|  | H Signal Pressure: | 1 | " wg | Inlet Duct PT: | 1 | " wg
|  | L Signal Pressure: | 0.84 | " wg | Inlet Duct PS: | 0.94679 | " wg
|  | Sensor ∆P: | 0.16 | " wg | Inlet Duct PV: | 0.05321 | " wg
|  | Altitude, ft: | 0 |  | K-Factor: | 2469
[5 empty] | Inlet Area: | 1.069 | ft2
DDC Controls
Pneumatic Controls
C51 Analog Controls

## Sensors Used (hidden)
Top input data
8 | 1 | [5 empty] | Altitude Corrected Signals
max CFM | 600 |  | Top input data |  | K-0 | K-ALT | Max | Min | Max | Min | VDC=m*CFM + b
min CFM | 250 |  |  | Inlet Size | Factor | Factor | dP | dP | vDC | vDC | m | b
MAX dp/VDC | 0.47892 |  |  | 10 | 1353 | 1353 | 0.19666 | 0.034142 | 4.3531 | 1.7383 | 0.0075 | -0.1299
MIN dp/VDC | 0.083146 |  |  | 12 | 1802 | 1802 | 0.11086 | 0.019247 | 3.5173 | 1.53 | 0.0057 | 0.111
kfactor | 867 |  |  | 14 | 2469 | 2469 | 0.059055 | 0.010253 | 2.5423 | 1.0083 | 0.0044 | -0.0878
inlet area | 0.34907 |  |  | 16 | 3366 | 3366 | 0.031774 | 0.0055163 | 1.5123 | 0.43152 | 0.0031 | -0.3418
|  |  |  | 24 x 16 | 6358 | 6358 | 0.0089056 | 0.0015461 | 0.91114 | 0.38818 | 0.0015 | 0.0147
|  |  |  | 5 | 287 | 287 | 4.3706 | 0.75878 | 19.2625 | 8.2106 | 0.0317 | 0.3177
Bottom input data |  |  |  | 6 | 469 | 469 | 1.6367 | 0.28414 | 12.6605 | 5.3042 | 0.0211 | 0.0499
14 | 1 |  |  | 7 | 612 | 612 | 0.96117 | 0.16687 | 9.3498 | 3.8064 | 0.0159 | -0.1537
input Altitude | 0 |  |  | 8 | 867 | 867 | 0.47892 | 0.083146 | 7.0997 | 2.8812 | 0.0121 | -0.1326
input dP | 0.16 |  |  | 9 | 1098 | 1098 | 0.29861 | 0.051841 | 5.4349 | 2.2274 | 0.0092 | -0.0639
Airflow Rate | 987.6
kfactor | 2469
inlet area | 1.069 |  | Bottom input data |  | K-0 | K-ALT | CFM @
|  |  |  | Inlet Size | Factor | Factor | dP
|  |  |  | 10 | 1353 | 1353 | 541.2
|  |  |  | 12 | 1802 | 1802 | 720.8
Altitude top data |  |  |  | 14 | 2469 | 2469 | 987.6
| Air | Correction |  | 16 | 3366 | 3366 | 1346.4
Altitude,ft | Density | Factor |  | 24 x 16 | 6358 | 6358 | 2543.2
0 | 0.075 | 1 |  | 5 | 287 | 287 | 114.8
500 | 0.074 | 0.98667 |  | 6 | 469 | 469 | 187.6
1000 | 0.072 | 0.96 |  | 7 | 612 | 612 | 244.8
1500 | 0.071 | 0.94667 |  | 8 | 867 | 867 | 346.8
2000 | 0.07 | 0.93333 |  | 9 | 1098 | 1098 | 439.2
2500 | 0.068 | 0.90667
3000 | 0.067 | 0.89333
3500 | 0.066 | 0.88 | Altitude bottom data
4000 | 0.065 | 0.86667 |  | Air | Correction
4500 | 0.064 | 0.85333 | Altitude,ft | Density | Factor
5000 | 0.062 | 0.82667 | 0 | 0.075 | 1
5500 | 0.061 | 0.81333 | 500 | 0.074 | 0.98667
6000 | 0.06 | 0.8 | 1000 | 0.072 | 0.96
6500 | 0.059 | 0.78667 | 1500 | 0.071 | 0.94667
7000 | 0.058 | 0.77333 | 2000 | 0.07 | 0.93333
0 | 0.074708 | 0.99611 | 2500 | 0.068 | 0.90667
|  |  | 3000 | 0.067 | 0.89333
|  |  | 3500 | 0.066 | 0.88
|  |  | 4000 | 0.065 | 0.86667
|  |  | 4500 | 0.064 | 0.85333
|  |  | 5000 | 0.062 | 0.82667
|  |  | 5500 | 0.061 | 0.81333
|  |  | 6000 | 0.06 | 0.8
|  |  | 6500 | 0.059 | 0.78667
|  |  | 7000 | 0.058 | 0.77333
|  |  | 0 | 0.074708 | 1

## User Guide
User Guide
1. This software is applicable for all Anemostat Air Terminals utilizing the patented Velocity Wing cross-type air flow sensor.
2. Compatable with Excel 2000 and later.
3. There are two data input windows. The top window will calculate flow parameters and sensor data by entering in the inlet size, air flow rates, and altitude if you wish to adjust for air density at the location.
4. Selecting the C51 Analog Control Type will cause the output data in the top window to display the controller voltage for the flow rates input. These voltages are adjusted at the wall thermostat to limit flow to the maximum and minimum flow rates entered, and are specific to the C51 analog controller only.
5. The bottom data input window requires sensor readings from the high and low sensor pressure ports. These can be determined using a manometer or magnehelic gauge. Because analog and digital controls typically use flow-thru sensing technology, the pneumatic signal lines should be removed from the controller to prevent signal pressure reduction. For accuracy, the damper actuator should be fixed in position for a steady state signal.
6. K-factors are based on Velocity Wing sensor signals determined using non-flow through measuring devices such as a manometer or magnehelic. Using K-factors as the flow constant for digital controllers using flow-thru sensors may not be applicable.
7. In top airflow data window, if signal values turn red when controller C51 is selected, these are out of range for the size selected or airflow rates entered. If the signal value turns red for DDC or pneumatic control types, these MAY be out of range, and are dependent upon the control device. See controller specifications to learn more about the operating range of the specific controller.
Disclaimer
This freeware is provided by Anemostat for personal use. Although every effort has been made to insure the accuracy and compatability of this program, Anemostat makes no claims as to its accuracy, and assumes no liability for its use.